*

*       <<<<<<<<  SWMM 4.3 EXTRAN DATA FILE >>>>>>>>>

*

* This file last updated 4/22/94 by WCH.

*

*	This is an input data file to the SWMM 4.3 (beta) Extran Block

*       for modeling the hydraulics of sewer or open channel systems.

*       All lines with an asterisk in column 1 are comment lines

*       and are ignored by the program.

*

*       Input data are free format and may be up to 230 columns wide.

*       You must have a value for every data column even if the program

*       will not actually use a given value.  There must be at least one

*       space or comma between every input value.  Alphanumeric data must

*       be enclosed in single quotes.

*

*       Caution!  Data lines that are "wrapped around" (continued on

*       two or more lines) should have a blank in column 1, unless a

*       card identifier is needed.

*

*       SWMM uses both U.S. customary units and metric units.  The

*       examples use feet, cfs, acres, inches and inches/hour.  If metric

*       is specified substitute meters, cms, hectares, millimeters and

*       millimeters/hour.  If metric is used, internal compuations in

*       the Extran Block are also performed in metric units.

*============================================================================

*	The SW card sets up the interface files to be used or created.

*	There is one output file (#8) that will contain the time series of

*       flows for subsequent blocks.  Remember, Extran does not perform

*       pollutant routing.  If pollutants are included on an input interface

*       file, they are ignored.

*============================================================================

*  NBLOCK  JIN(1)  JOUT(1)

SW    1      0       8

*============================================================================

*   The MM card opens the scratch files to be used by different subroutines.

*   A certain number (up to 4 for EXTRAN) may be required for each block.

*============================================================================

*  NITCH  NSCRAT(1)  NSCRAT(2)  NSCRAT(3)  NSCRAT(4)

MM   4       1          2          3          4

*============================================================================

*     The @ command is used to save an interface or scratch file

*     permanently, or to access a previously saved file.  This line should

*     be placed before the first SWMM block call.  The format of the @

*     command is as follows:

*============================================================================

*Column 1    Unit number of the       Name of the interface

*            interface file saved     file (any valid DOS filename)

*            or utilized

*

*@             8                        'EXDOC.DNT'

*============================================================================

*Column 1

* $ANUM  ==> Use alphanumeric labels for subcatchment and channel/pipe

*            labels -- WHEREVER ENCOUNTERED AND IN ALL PRIOR AND SUBSEQUENT

*            BLOCKS.  Names (IDs) must be enclosed in single quotes.  A

*            maximum length of 6 characters for a label is recommended.

*            Longer names (max. of 8 characters) may not print out correctly

*            but will be input OK.

*============================================================================

*Column 1

* $NOQUOTE ==> Omit on-screen and printed literary quotations in SWMM output.

*============================================================================

$EXTRAN         	Call the EXTRAN Block with a '$' in first column.

*============================================================================

*	Create title lines for the simulation.  There are two title lines

*       for the EXTRAN Block.  Titles are enclosed in single quotes.

*============================================================================

A1 'EXTRAN EXAMPLE SHOWING MOST CONDUIT TYPES'

A1 'INITIAL 20 CFS IN TWO NATURAL CHANNELS'

*============================================================================

*   'B' data lines describe the Extran program control information.

*============================================================================

*   'B0' data line is optional and need not be entered by the user.

*============================================================================

*    B0 line    :

*       ISOL    : Solution technique parameter (see Appendix C).

*                 = 0 Explicit solution of Section 5 (default),

*                 = 1 Enhanced explicit solution,

*                 = 2 Iterative explicit solution using variable

*                     time-steps <_ DELT (group B1).  Iteration

*                     limit is ITMAX and convergence criterion is

*                     SURTOL (group B2).

*       KSUPER  : = 0 Use minimum of normal flow and dynamic flow

*                     when water surface slope  < conduit slope (default).

*                 = 1 Normal flow always used when flow is supercritical.

*============================================================================

*  ISOL  KSUPER

B0  0      0

*============================================================================

*  'BB' data line is optional and need not be entered by the user.

*============================================================================

*     BB line :

*      JELEV  :  Input elevations instead of depth for variables ZP1

*                and ZP2 on data line C1.

*                = 0  Enter conduit depth offset (ZP values), default.

*                = 1  Enter absolute elevation of conduit offset.

*      JDOWN  :  = 0  Use either minimum of normal or critical depth

*                     at outfall conduits.  This is the default.

*                = 1  Use critical depth at outfall conduits.

*                = 2  Use normal depth at outfall conduits.

*============================================================================

*   JELEV   JDOWN

BB     0       0

*============================================================================

*     B1 line :

*       NTCYC : Number of time-steps desired.

*       DELT  : Length of time-step, seconds.  Shorten to improve stability

*               if necessary, but must have DELT >_ 1 sec.  Values < 5 sec

*               should be avoided if possible by using equivalent pipes to

*               avoid violation of Courant stability condition.

*       TZERO : Start time of simulation, decimal hours.  Time zero

*               is midnight (beginning) of first simulation day.

*       NSTART: First time-step to begin print cycle.

*       INTER : Interval between intermediate print cycles during

*               simulation.  Number of cycles printed is

*               (NTCYC - NSTART)/INTER.

*       JNTER : Interval between time-history summary print cycles at end

*               of simulation.  Number of cycles printed is NTCYC/JNTER.

*       REDO  : Hot-start file manipulation parameter.

*               = 0  No hot-start file is created or used,

*               = 1  Read NSCRAT(2) for initial flows, heads,

*                    areas, and velocities,

*               = 2  Create a new hot-start file on NSCRAT(2),

*               = 3  Create a new hot-start file but use the old

*                    file as the initial conditions.  The old file

*                    is subsequently erased and a new file created.

*

*   Note, the following new (4/11/94) parameter is strictly optional and

*   may be omitted from B1 line without error.

*

*       IDATZ : Initial date of simulation, 6 digits, yr/mo/day.

*               Default is 880101.

*============================================================================

*   NTCYC DELT  TZERO NSTART INTER JNTER REDO IDATZ

B1  720   20.0   0.0   180    300    15   0   940101

*B1  720   20.0   0.0   180    300    15   0

*============================================================================

*     B2 line :

*      METRIC : U.S. customary or metric units for input/output.

*               = 0  U.S. customary units.

*               = 1  Metric units.

*      NEQUAL : Modify short pipe lengths using an equivalent pipe.

*                 to ease time step limitations (see equation 2-3).

*               = 0  Do not modify.

*               = 1  Modify short pipe lengths.  This creates longer

*                    pipes with correspondingly lower roughness.

*                    Note: because the cross-section dimensions stay the

*                    same, this results in an increase in volume in the

*                    network.  If the user wishes, the user can input

*                    an alternative equivalent pipe/channel according

*                    to different criteria, e.g., constant volume.

*      AMEN   : Default surface area for all manholes ft2 [m2].

*               Used for surcharge calculations in Extran.

*               Manhole default diameter is 4 ft (1.22 m).

*      ITMAX  : Maximum number of iterations to be used in surcharge

*               and iterative calculations (30 recommended for ISOL

*               0 and ISOL 1; 10 recommended for ISOL 2).

*      SURTOL : Fraction of average flow in surcharged areas

*               to be used as convergence criterion for surcharge

*               iterations (0.05 recommended).  Also, convergence

*               criterion during flow iterations (ISOL = 2) with

*               0.0025 recommended.

*============================================================================

*   METRIC NEQUAL  AMEN ITMAX SURTOL

B2     0     0     0.0   30    0.05

*============================================================================

*     B3 line :

*      NHPRT  : Number of junctions for detailed printing

*               of head output (30 nodes max., can be modified by

*               recompiling and altering parameter NPO on 'TAPES.INC').

*      NQPRT  : Number of conduits for detailed printing

*               of discharge output (30 conduits max.).

*      NPLT   : Number of junction heads to be plotted (30 max.).

*      LPLT   : Number of conduits for flows to be plotted (30 max.).

*      NJSW   : Number of input junctions (data group K2), if

*               user input hydrographs are used (65 max., can be modified

*               by recomiling and altering parameter NEH on 'TAPES.INC').

*============================================================================

* NHPRT NQPRT NPLT LPLT NJSW

B3   5    5    4    4    3

*============================================================================

*     B4 line :  Required only if NHPRT > 0 on data group B3.

*     JPRT(1) :  First junction number/name for detailed printing

*                of junction elevations.

*                Continue for the number of nodes defined by NHPRT.

*============================================================================

*  JPRT1 JPRT2  etc.

B4 30002 30004 30006 30081 30082

*============================================================================

*     B5 line :  Required only if NQPRT > 0 on data group B3.

*     CPRT(1) :  First conduit number/name for detailed printing

*                of conduit flow and velocity.

*                Continue for the number of conduits defined by NQPRT.

*============================================================================

*  CPRT1 CPRT2  etc.

B5 10001 10003 10005 10081 10082

*============================================================================

*     B6 line :  Required only if NPLT > 0 on data group B3.

*     JPLT(1) :  First junction number/name for detailed plotting

*                of junction elevations.

*                Continue for the number of nodes defined by NPLT.

*============================================================================

*  JPLT1 JPLT2  etc.

B6 30002 30006 30081 30082

*============================================================================

*     B7 line :  Required only if LPLT > 0 on data group B3.

*     KPLT(1) :  First conduit number/name for detailed plotting

*                of conduit flow.

*                Continue for the number of conduits defined by LPLT.

*============================================================================

*  KPLT1 KPLT2  etc.

B7 10001 10006 10081 10082

*============================================================================

*     Data group B8 is optional and may be omitted.

*============================================================================

*     B8 line :

*     NSURF   : Number of conduit upstream/downstream elevation plots.

*               The upstream/downstream heads are plotted on

*               the same graph.

*     JSURF(1): First conduit number/name for plotting.

*               Continue for the number of conduits defined by NSURF.

*============================================================================

*   NSURF  JSURF1  JSURF2  etc.

B8    2    10081   10082

*============================================================================

*     'C' data lines describe the conduit links in EXTRAN.

*============================================================================

*     C1 line  :

*     NCOND    : Conduit number (any valid integer), or

*                conduit name (enclose in single quotes).

*     NJUNC(1) : Junction number at upstream end of conduit, or

*                junction name (enclose in single quotes).

*     NJUNC(2) : Junction number at downstream end of conduit, or

*                junction name (enclose in single quotes).

*     QO       : Initial flow, ft3/s [m3/s].

*     NKLASS   : Type of conduit shape.

*                = 1  Circular.

*                = 2  Rectangular.

*                = 3  Horseshoe.

*                = 4  Egg.

*                = 5  Baskethandle.

*                = 6  Trapezoidal channel.

*                = 7  Parabolic/power function channel.

*                = 8  Irregular (natural) channel.

*                     Note: A negative NKLASS(N) creates a flap gate

*                          that will only let water move from the

*                          downstream (lower elevation) node to

*                          the upstream node.

*     AFULL    : Cross sectional area of conduit, ft2 [m2],

*                enter only for types 3, 4, and 5.  (Geometric

*                properties for types 3-5 may be found in Section

*                6 of the main SWMM User's Manual.)

*     DEEP     : Vertical depth (diameter for type 1)

*                of conduit, ft [m].  Not required for type 8.

*     WIDE     : Maximum width of conduit, ft [m].

*                Bottom width for trapezoid, ft [m].

*                Top width for parabolic/power function, ft [m].

*                Not required (N.R.) for types 1 and 8.

*     LEN      : Length of conduit, ft [m].

*                N.R. for type 8.  Enter in data group C3.

*

*                Note: A negative LEN(N) creates a flap gate

*                      that will only let water move from the

*                      upstream (higher elevation) node to the

*                      downstream node.

*     ZP(1)    : Distance of conduit invert above junction invert

*                at NJUNC(1), ft [m].

*     ZP(2)    : Distance of conduit invert above junction invert

*                at NJUNC(2), ft [m].

*                Note: If JELEV on line BB is 1 then ZP(1) and ZP(2)

*                      are actual elevations.

*     ROUGH    : Manning coefficient (includes entrance, exit,

*                expansion, and contraction losses).  N.R. for

*                type 8.  Uses XNCH in data group C2.

*     STHETA   : Slope of one side of trapezoid.  Required only for

*                type = 6, (horizontal/vertical; 0 = vertical walls).

*                For type 7, the channel exponent( 2.0, 3.0, etc.).

*                For type 8, the cross-section identification number

*                (SECNO, group C3) of the cross section used for

*                this EXTRAN channel.  Unlike HEC-2, EXTRAN uses only

*                a single cross section to represent a natural

*                channel reach for type 8 channels.  A negative

*                STHETA(N) will eliminate the printing of the dimension-

*                less curves associated with each natural channel or

*                power-function channel.

*     SPHI     : Slope of other side of trapezoid. Required only for

*                type = 6, (horizontal/vertical; 0 = vertical walls).

*                The average channel slope for type 8. This slope

*                is used only for developing a rating curve for

*                the channel.  Routing calculations use invert

*                elevation differences divided by length.

*============================================================================

*   NCOND NJ1 NJ2    QO  NKLASS AFULL DEEP WIDE  LEN   ZP1 ZP2 ROUGH STHETA SPHI

C1 10001 30001 30002  0.   1    0.0   3.0  0.0   510.  0.0 0.0 0.015  0.0   0.0

C1 10002 30002 30003  0.   2    0.0   3.0  3.5   520.  0.0 0.0 0.015  0.0   0.0

* GEOMETRIC PROPERTIES OF HORSESHOE, EGG AND BASKET-HANDLE ARE IN

*  SECTION 6 OF MAIN SWMM MANUAL.

C1 10003 30003 30006  0.   3   13.26  4.0 4.0    530. 0.0 0.0  0.015  0.0   0.0

C1 10004 30004 30005  0.   4    8.17  4.0 2.67   540. 0.0 0.0  0.015  0.0   0.0

C1 10005 30005 30006  0.   5   12.58  4.0 3.78   550. 0.0 1.0  0.015  0.0   0.0

C1 10007 30007 30006  0.   7    0.0   3.0 4.0    570. 0.0 2.0  0.018  0.0   0.0

C1 10006 30006 30081  0.   6    0.0   5.0 8.0    560. 0.0 0.0  0.020 0.25  0.25

*  Conduit 10081 uses data from section 91

C1 10081 30081 30082 20.   8    0.0   5.0 0.0   1000. 0.0 0.0  0.0    91  0.001

*  Conduit 10082 uses data from section 92

*          A negative STHETA stops the printout of the

*             normalized curves for a natural channel.

C1 10082 30082 30083 20.   8    0.0   5.0 0.0   1000. 0.0 0.0  0.0    92  0.002

*============================================================================

*        The C2 (NC), C3 (X1), and C4 (GR) data lines are for any type 8

*   conduit.  They follow as a group after all C1 lines have been entered.

*   The sequence for channels must be in the same order as the earlier

*   sequence of type-8 C1-lines.  The same cross-sectional information on

*   lines C2-C4 can be used by more than one channel.  I.e., different

*   channels can have the same STHETA values.

*

*        Data groups C2, C3 and C4 correspond to HEC-2 lines NC,

*   X1 and GR.  HEC-2 input may be used directly if desired.  Lines

*   may be identified either by EXTRAN identifiers (C2, C3, C4) or

*   HEC-2 identifiers (NC, X1, GR).

*============================================================================

*        The C2 line is used to input natural channel roughness.

*   This is an optional data line that permanently modifies the Manning's

*   roughness coefficients (n) for the remaining natural channels.  This

*   data group may repeated for later channels.  It must be included for

*   the first natural channel modeled.

*============================================================================

*   C2 or NC line :

*         XNL     : n for the left overbank.

*                   = 0.0  No change.

*                   > 0.0  New Manning's n.

*         XNR     : n for the right overbank.

*                   = 0.0  No change.

*                   > 0.0  New Manning's n.

*         XNCH    : n for the channel.

*                   = 0.0  No change.

*                   > 0.0  New Manning's n.

*                   Note:  XNCH is used to develop the normalized

*                          flow routing curves.  Tabulated values

*                          of hydraulic radius account for variability

*                          of n when a constant n (XNCH) is used

*                          during the flow routing process.

*============================================================================

*    XNL   XNR   XNCH

C2  0.08  0.08   0.03

*============================================================================

* C3 or X1 line : Cross Section Data. Required for each type 8

*                  conduit in earlier C1 data lines.

*     SECNO     : Cross section identification number (corresponding to

*                 STHETA value on C1 lines).

*     NUMST     : Total number of stations on the following

*                 C4 (GR) data lines.  NUMST must be < 99.

*     STCHL     : The station of the left bank of the channel,

*                 ft [m].  Must be equal to one of the STA numbers

*                 on the C4 (GR) data lines.

*     STCHR     : The station of the right bank of the channel,

*                 ft [m].  Must be equal to one of the STA

*                 on the C4 (GR) data lines.

*     XLOBL     : Not required for EXTRAN (enter 0.0).

*     XLOBR     : Not required for EXTRAN (enter 0.0).

*     LEN       : Length of channel reach represented

*                 by this cross section, ft [m].

*     PXSECR    : Factor to modify the horizontal dimensions

*                 for a cross section.  The distances between

*                 adjacent C4 (GR) stations (STA) are multiplied by

*                 this factor to expand or narrow a cross section,

*                 including STCHL and STCHR on this line.

*                 The STA of the first C4 (GR) point remains the same.

*                 The factor can apply to a repeated cross section

*                 or a current one.  A factor of 1.1 will increase

*                 the horizontal distance between the C4 (GR) stations

*                 by 10 percent.  Enter 0.0 for no modification.

*     PSXECE    : Constant to be added (+ or -) to C4 (GR)

*                 elevation data on next C4 (GR) line.  Enter

*                 0.0 to use C4 (GR) values as entered.

*============================================================================

* SECNO NUMST STCHL STCHR XLOBL XLOBR LEN PXCECR PSXECE

C3 91    6    50.0  110.0  0.0   0.0  1000. 0.0   799.0

*============================================================================

* C4 or GR line : Cross Section Profile. Required for each type 8 conduit.

*     EL(1)     : Elevation of cross section at STA(1).  May be

*                 positive or negative, ft [m].

*     STA(1)    : Station of cross section 1, ft [m].

*     EL(2)     : Elevation of cross section at STA(2), ft [m].

*     STA(2)    : Station of cross section 2, ft [m].

*

*        Enter NUMST elevations and stations to describe the cross section.

*  Enter 5 pairs of elevations and stations per data line.  (Include group

*  identifier, C4 or GR, on each line.)  Stations should be in increasing

*  order progressing from left to right across the section.  Cross section

*  data are traditionally oriented looking downstream (HEC, 1982).

*============================================================================

*  EL1  STA1  EL2  STA2  EL3  STA3  EL4  STA4   EL5  STA5

C4 5.0  0.0   4.0  50.0  1.0  55.0  0.0  100.0  3.0  110.0

*  EL6  STA6

C4 5.0  150.0

*  OTHER NATURAL CHANNEL

C3 92    6    55.0  115.0  0.0   0.0  1000. 0.0   798.0

C4 5.0  0.0   4.5  55.0  0.0  60.0  2.0  95.0   4.0  115.0

C4 6.0  160.0

*============================================================================

*     The 'D1' data line describes the junction nodes in EXTRAN.

*============================================================================

*     D1 line  :

*     JUN      : Junction number (any valid integer), or

*                junction name (enclose in single quotes).

*     GRELEV   : Ground elevation, ft [m].

*     Z        : Invert elevation, ft [m].

*     QINST    : Net constant flow into junction, cfs [m3/s].

*                Positive indicates an inflow.

*                Negative indicates a withdrawl or loss.

*     YO       : Initial depth above junction invert elevation,

*                ft [m].

*============================================================================

*    JUN   GRELEV   Z   QINST  Y

D1 30001   810.0  802.0  0.0  0.0

D1 30002   810.0  801.0  0.0  0.0

D1 30003   810.0  800.5  0.0  0.0

D1 30004   810.0  802.5  0.0  0.0

D1 30005   810.0  801.5  0.0  0.0

D1 30007   806.0  803.0  0.0  0.0

D1 30006   806.0  800.0  0.0  0.0

* INPUT 20 CFS AT BEGINNING OF NATURAL CHANNELS (E.G., RECEIVING STREAM)

D1 30081   806.0 799.0  20.   1.5

D1 30082   806.0 798.0  0.0   1.5

* INITIAL CONDITION OF 2 FT DEPTH AT DOWNSTREAM END (CONSTANT HEAD)

D1 30083   806.0 796.0  0.0   2.0

*============================================================================

*     The 'E1' data line describes storage junctions in EXTRAN.

*          Note: Each storage junction must also have been

*                 entered in the junction data (Group D1).

*          There are three types of storage junctions:

*                (1) Constant storage area.  Only JSTORE, ZTOP and ASTORE

*                    are required on line E1.  Line E2 is not required.

*                (2) Variable storage area.  JSTORE, ZTOP, ASTORE and

*                    NUMST are required on line E1.  NUMST values on

*                    line E2 are necessary.

*                (3) Power function storage area.  JSTORE, ZTOP, ASTORE

*                    and NUMST are required on line E1.  There should be

*                    two data values on line E2.

*============================================================================

*     E1 line  :

*     JSTORE   : Junction number containing storage facility, or

*                junction name (enter in single quotes).

*     ZTOP     : Junction crown elevation (must be higher than crown

*                of highest pipe connected to the storage junction), ft [m].

*     ASTORE   : Storage volume per foot (or meter) of depth

*                (i.e., constant surface area) ft3/ft [m3/m].

*                Set ASTORE(J) < 0 to indicate a variable-area

*                storage junction.  ASTORE may be any value for power

*                function storage junction.

*     NUMST    : Total number of stage/storage area points on following

*                E2 data lines.  NUMST < 30.   Enter a value of -2 for

*                NUMST to generate area vs. stage using a power function.

*                NUMST required only if ASTORE < 0 and for power function

*                variable storage areas.

*============================================================================

*                      Line E2 variable storage data.

*     Variable-Area Storage Junction, Stage vs. Surface Area Points.

*============================================================================

*     E2 line     :

*     QCURVE(1,1) : Surface area of storage junction at depth point # 1,

*                   acres [hectares].  If NUMST equals -2 this is the

*                   coefficient of the power function.

*     QCURVE(2,1) : Depth above junction invert at point 1, ft [m].

*                   If NUMST equals -2 this is the exponent of the

*                   power function and is the last value entered.

*

*                   Repeat for NUMST pairs of values if NUMST > 0.

*                   If more than one line is required leave the first

*                   two columns blank in the second etc. line.

*============================================================================

*        The 'F1' data line contains EXTRAN orifice data (Max of 60).

*============================================================================

*     F1 line     :

*     NJUNC(1)    : Junction number containing orifice, or

*                   junction name (enter in single quotes).

*     NJUNC(2)    : Junction number to which orifice discharges, or

*                   junction name (enter in single quotes).

*     NKLASS      : Type of orifice.

*                    =  1 Side outlet.

*                    =  2 Bottom outlet.

*                    = -1 Time-history side outlet orifice

*                         with data entered on data group F2.

*                    = -2 Time-history bottom outlet orifice,

*                         with data entered on data group F2.

*     AORIF       : Orifice area, ft2 [m2].

*     CORIF       : Orifice discharge coefficient.

*     ZP          : Distance of orifice invert above junction

*                   floor (define only for side outlet orifices), ft [m].

*============================================================================

*           Enter time-history orifice data on line F2.

*           Each F2 line follows the appropriate F1 line.

*============================================================================

*     F2 line     :

*     NTIME       : Number of data points to describe the time

*                   history of the orifice (50 max.).

*     VORIF(1,1)  : First time, hours, that the orifice discharge

*                   coefficient and area change values from intial

*                   settings of group F1 above.  Time zero refers to

*                   beginning (midnight) of beginning day of simulation.

*                   E.g., VORIF(I,1,1) = 22.0 means first change in

*                   orifice setting occurs at 10:00 p.m. on first day of

*                   simulation.  Increase hours past 24 (e.g., 25, 26)

*                   for multi-day simulations.

*     VORIF(1,2)  : First new value of orifice discharge coefficient.

*     VORIF(1,3)  : First new value of orifice area.

*

*                   Repeat for NTIME values of time/coefficient/area.

*                   Only one F2 group identifier is required, on the

*                   first data line.  Subsequent lines (if required)

*                   should not include F2 identifier.

*============================================================================

*        The 'G1' data line contains EXTRAN weir data (Max of 60).

*============================================================================

*     G1 line     :

*     NJUNC(1)    : Junction number at which weir is located, or

*                   junction name (enter in single quotes).

*     NJUNC(2)    : Junction number to which weir discharges, or

*                   junction name (enter in single quotes).

*                   Note: To designate outfall weir, set NJUNC(N,2)

*                         equal to zero or ' ' (one space between quotes).

*     KWEIR       : Type of weir.

*                   = 1 Transverse (exponent = 3/2).

*                   = 2 Transverse with tide gate.

*                   = 3 Side flow (exponent = 5/3).

*                   = 4 Side flow with tide gate.

*     YCREST      : Height of weir crest above invert, ft [m].

*     YTOP        : Height to top of weir opening above invert

*                   (surcharge level) ft [m].

*     WLEN        : Weir length, ft [m].

*     COEF       :  Coefficient of discharge for weir.

*============================================================================

*        The 'H1' data line contains EXTRAN pump data (Max of 20).

*============================================================================

*     H1 line     :

*     IPTYP       : Type of pump.

*                   = 1 Off-line pump with wet well (program will

*                       set pump junction invert to -100).

*                       Note:  ONLY ONE PIPE CAN BE CONNECTED TO A

*                              TYPE 1 PUMP NODE.

*                   = 2 In-line lift pump.

*                   = 3 Three-point head-discharge pump curve.

*     NJUNC(1)    : Junction number being pumped, or

*                   junction name (enter in single quotes).

*     NJUNC(2)    : Pump discharge goes to this junction number, or

*                   junction name (enter in single quotes).

*     PRATE(1)    : Lower pumping rate, ft3/s [m3/s].

*     PRATE(2)    : Mid-pumping rate, ft3/s [m3/s].

*     PRATE(3)    : High pumping rate, ft3/s [m3/s].

*     VRATE(1)    : If IPTYP = 1  enter the wet well volume for

*                            mid-rate pumps to start, ft3 [m3].

*                   If IPTYP = 2  enter the junction depth for

*                                 mid-rate pumps to  start, ft [m].

*                   If IPTYP = 3 enter the head difference (head at

*                      junction downstream of pump minus head at

*                      junction upstream of pump) associated with the

*                      lowest pumping rate, ft [m].  (This will be the

*                      highest head difference.)

*     VRATE(2)    : If IPTYP = 1 enter the wet well volume for

*                      high-rate pumps to start, ft3 [m3].

*                   If IPTYP = 2  enter the junction depth for

*                      high-rate pumps to start, ft [m].

*                   If IPTYP = 3 enter the head difference associated

*                      with the mid-pumping rate, ft [m].

*

*                   Note: A non-zero VRATE(I,3) and VWELL(I) are

*                                required only if IPTYP = 1 or 3.

*

*     VRATE(3)    : If IPTYP = 1 enter total wet well capacity, ft3 [m3].

*                   If IPTYP = 3 then enter the head difference associated

*                      with highest pumping rate, ft [m].  (This will be

*                      the lowest head difference.)

*     VWELL       : If IPTYP = 1 then enter initial wet well volume, ft3 [m3].

*                   If IPTYP = 3 then enter the initial depth in the pump

*                      inflow junction, ft [m].

*

*                   Note: Enter PON(I) and POFF(I) only if IPTYP = 3.

*

*     PON         : Depth in pump inflow junction to turn pump on, ft [m].

*     POFF        : Depth in pump inflow junction to turn pump off, ft [m].

*============================================================================

* IPTY NJUNC  NJUNC  PRATE1  PRATE2 PRATE3 VRATE1 VRATE2 VRATE3  VWELL  PON  POFF

**H1   3  401    301   10.0     50.0   100.0   70.0   60.0  50.0   5.00  6.00  2.00

*============================================================================

*     'I' data lines list the outfall junctions in Extran.

*           I1 - Outfalls without tide gates (1 line/outfall, 25 Max)

*           I2 - Outfalls with tide gates (1 line/outfall, 25 Max)

*         Note : for groups I1 and I2, enter junction name in single quotes

*                if the alphanumeric option is being used.

*         Note : ONLY ONE CONNECTING CONDUIT IS PERMITTED TO AN OUTFALL NODE.

*============================================================================

*     I1 line     :

*     JFREE       : Number/name of outfall junctions without tide gate

*                   (no back-flow restriction).

*     NBCF        : Type of boundary condition from the sequence of

*                   data group lines J1 - J4.  E.g., if NBCF = 2, use the

*                   boundary condition indicated by the second group of

*                   J1 - J4 lines.

*============================================================================

* FREE OUTFALL TO CONSTANT HEAD AT DOWNSTREAM END

*    JFREE  NBCF

I1   30083   1

*============================================================================

*     I2 line     :

*     JGATE       : Number/name of outfall junctions with tide gate

*                   (back-flow restriction).

*     NBCG        : Type of boundary condition from the sequence of

*                   data group lines J1 - J4.

*============================================================================

*    JGATE  NBCG

*I2

*============================================================================

*      Boundary condition data are entered on the 'J' lines.

*          Note: Repeat sequence of data groups J1-J4 for up to 20

*                different boundary conditions.  Appearance in sequence

*                (e.g., first, second... etc..) determines the value for

*                NBCF and NBCG in data groups I1 and I2.

*============================================================================

*     J1 line  :

*     NTIDE    : Boundary condition index.

*                = 1 No water surface at outfalls (elevated discharge).

*                    J2, J3 and J4 lines are not required.

*                = 2 Controlling water surface at outfall at a constant

*                    elevation A1 (group J2), ft [m].

*                = 3 Tide coefficients (group J2) provided by user.

*                = 4 Program will compute tide coefficients.

*                = 5 Stage-history of water surface elevations input

*                    by user.  Program uses linear interpolation

*                    between data points.

*============================================================================

*  NTIDE

J1   2

*============================================================================

*     J2 line   : Stage and/or Tidal Coefficients.

*                 Note : NOT REQUIRED (OMIT) IF NTIDE(I) = 1 OR

*                                            5 ON DATA GROUP J1.

*     A1        : First tide coefficient, ft [m].

*                 Constant elevation of NTIDE = 2 on line J1.

*

*         Note, no further parameters required if NTIDE = 2.

*

*     W         : Tidal period, hours. Required only if NTIDE(I) = 3 or 4.

*                 Note : The next six fields are not required unless

*                        NTIDE(I) = 3 on line J1.  See equation 2-14

*                        for the definition of coefficients.

*     A2        : Second tide coefficient, ft [m].

*     A3        : Third tide coefficient, ft [m].

*     A4        : Fourth tide coefficient, ft [m].

*     A5        : Fifth tide coefficient, ft [m].

*     A6        : Sixth tide coefficient, ft [m].

*     A7        : Seventh tide coefficient, ft [m].

*============================================================================

*   A1    W    A2  A3  A4  A5  A6  A7

J2 798.0

*============================================================================

*     J3 line   : Tidal/Stage Information if NTIDE = 4 or 5 on line J1.

*

*     KO        : Type of tidal input.

*                 = 0 Input is in the form of a time series of NI tidal

*                     heights.  This parameter is not used if NTIDE equals 5.

*                 = 1 Input is in the form of the high and low water

*                     values found in the tide tables,

*                     (HHW, LLW, LHW and HLW).  NI must be 4.

*     NI        : Number of information points.

*     NCHTID    : Tide information print control.

*                 = 0 Do not print information.

*                 = 1 Print information on tide coefficients

*                     or stage history.

*     DELTA     : Convergence criterion (default = 0.0005) for fitting

*                 the tidal function, ft [m].  Not required for NTIDE = 5.

*============================================================================

*J3

*============================================================================

*     J4 line   : Time and stage information if NTIDE = 4 or 5 on line J1.

*     TT        : Time of day, first information point, hours.

*                 (Increase hours past 24 if necessary.)

*     YY        : Tide/stage at time above, ft [m].

*                  Note: Enter 5 pairs of time and stage information per

*                        data line until NI points are listed.  Include

*                        group identifier on each line.

*============================================================================

*J4

*============================================================================

*      'K' data lines contain user input hydrograph information.

*                 Enter data only if NJSW > 0 on line B3.

*============================================================================

*     K1 line   :

*     NINC      : Number of input nodes and flows per line on line K3.

*============================================================================

*  NINC

K1  3

*============================================================================

*     K2 line   : Hydrograph Nodes.

*     JSW       : First input node number for line hydrograph, or

*                 node name (enter in single quotes).

*                 Note : Enter NINC nodes per line until NJSW nodes

*                        are entered.  (Repeat the group identifier

*                        on each line.)

*============================================================================

*      JSW1   JSW2   JSW3    etc.

K2     30001  30004  30007

*============================================================================

*     K3 line   : User Input Hydrographs.

*     TEO       : Time of day, decimal hours.

*     QCARD(1)  : Flow rate for first input node, JSW(1),

*                                           ft3/s [m3/s].

*                 Note : Enter TEO plus NJSW flows.  Enter TEO only on

*                        the first line of multiple ("wrapped around")

*                        lines.  Do not include group identifier K3 on

*                        lines that are "wrapped around."  Repeat the

*                        sequence for each TEO time.  Times do not have

*                        to be evenly spaced; linear interpolation is

*                        used to interpolate between entries.  The last

*                        K3 line will signal the end of the user

*                        hydrograph input.  The last TEO value should be

*                        > length or = length of simulation.  Increase TEO

*                        past 24.0 for multi-day simulations.

*==============================================================================

* INPUT ZERO FLOW FOR 1 HR TO LET CONSTANT INFLOW INTO NATURAL CHANNELS

* "WARM UP" THE NATURAL RIVER SECTIONS.  START TRIANGULAR HDYROGRAPHS AT

* THREE UPSTREAM ENDS OF SEWERS AT TIME = 1 HR.

*==============================================================================

*   TEO  QCARD(1) QCARD(2) QCARD(3)    Single line entry.

K3  0.0   0.0     0.0      0.0

K3  1.0   0.0     0.0      0.0

K3  1.5  15.0    18.0      9.0

K3  2.1   0.0     0.0      0.0

K3  4.0   0.0     0.0      0.0

*==============================================================================

*               End your input data set with a $ENDPROGRAM and a <CR>

$ENDPROGRAM